## 4264
PV&N TECHNICAL SERVICE LIMITED COMPANY (PV&N TECH.) Add: 12/12 Tran Anh Tong, Rach Dua Ward, Ho Chi Minh, Viet Nam Tel/Fax: (+84) 254 3 840 989 Mobile: 0937 08 80 81 Email: info@pvn-tech.com Website: www.pvn-tech.com
YÊU CẦU BÁO GIÁ/REQUEST FOR QUOTATION
Công ty/Company: |  |  | Người gửi/Send by:
Người nhận/Receive by: |  |  | Điện thoại/Phone:
Mã số thuế/ Tax code: |  |  | Email:
Điện thoại/Phone: |  |  | Ngày/Date:
Dự án/Project: |  |  | Số yêu cầu/RFQ No:
Chúng tôi muốn gửi tới quý công ty yêu cầu báo giá như chi tiết dưới đây/We would like to send you the request for quotation as details bellow.
NO | Name of product | Technical Descripton | Unit | Q'ty | U.Price (USD) | Amount (USD) | Manufacture | Origin | Year of Production
1 | Battery 12V 200Ah | For starting motors, sealed lead acid battery, maintennance-free, c/w bolts, terminals and connectors, 12V; 200Ah; CCA 1000A; Dimension 510 x 275 x 238mm; Battery life: 4 years or more. Refer to Model: Delkor N200 or equivalent. | Pce | 34,00
2 | Valve Regulated Lead Acid battery 12V; 50Ah c/w bolts and connectors | Sealed Lead-Acid Battery (VRLA): Voltage: 12V Capacity: 50Ah (Ampere-hours) Included Accessories: Comes with bolts and terminal connectors Dimensions: Length (261mm) x Width (174mm) x Height (217mm) Terminal Type: M8 Service Life: 10–12 years Internal Resistance: Less than 8.3mOhm Design Standards: Compliant with IEC 60896-21/-22 (international standards for VRLA batteries) Reference Model: Fiamm 12SLA50L or equivalent. | Pce | 36,00
3 | Ni Cd 2 cell/block; 1.2V; 165Ah | Nickel-cadmium (Ni-Cd) batteries; 1.2V; 165Ah; c/w bolts and connectors; life cycle that can last 20 years or more; Dimension HxWxL = 411x195x127mm; Terminal: M10; Internal resistance 1.54 mOhm; Designed in accordance with IEC 60623; Technical equal: SBLE 165-2, Saft | Set | 46,00
4 | Valve Regulated Lead Acid battery 9Ah; 12V c/w bolts and connectors | Type battery: 12V, 9AH; Valve regulated lead acid compliance with IEC 60896 part 22 or BS 6290 part 4. Eurobat long life 10 years. Electrolyte fully absorbed in glass mat “AGM” separator with extremely high micro porosity; Flame retardant plastics compliance with ABS IEC 707 or UL 94; Short circuit current over 600A; Weight: >=2.7 kg. internal resistance ≤ 23.6 mOhm; Dimension: L<=151xW<=65xH<94mm. Refer to model: Fiamm 12FGHL34/ Fiamm or or equivalent. | Pce | 242,00
5 | Battery 12V- 18AH | Valve Regulated Lead Acid (VRLA): Voltage: 12V Capacity: 18Ah (Ampere-hours) Included Components: Supplied with bolts and terminal connectors Dimensions: Length (181mm) xWidth (76mm) x Height(167mm) Terminal Type: M5/M6 Service Life: 10 years Typical Internal Resistance: ~18mOhm Design Standards: Compliant with IEC 60896-21/-22 (international standards for VRLA batteries) Reference Model: Fiamm 12FGL18 or equivalent. | Pce | 32
6 | Valve Regulated Lead Acid battery 42Ah; 12V c/w bolts and connectors | 12V, 40-42AH; Valve regulated lead acid compliance with IEC 60896 part 22 or BS 6290 part 4; Eurobat long life 10 years; Electrolyte fully absorbed in glass mat "AGM" separator with extremely high micro porosity; Flame retardant plasticscompliance with ABS IEC 707 or UL 94; Short circuit current over 600A; Weight: >=9.4 kg. Dimension: L<=197xW<=165xH<170mm. Refer to model : Fiamm 12SP42 or equal | Pce | 92,00
7 | Battery 12V, 70Ah sealed type | Valve Regulated Lead Acid battery (AGM) technology 12V; 70Ah c/w bolts and connectors; Dimension L (268) x W (174) x H(190) x Tol.H(194); Terminal: M8; Internal resistance lower than 7,3mOhm | Pce | 24,00
8 | Valve Regulated Lead Acid battery 12V; 110Ah c/w bolts and connectors | Valve Regulated Lead Acid battery (AGM) technology 12V; 110Ah c/w bolts and connectors; Dimension ( W x H x D) 379 x 217 x 174 mm; Terminal: M8; Design life: 10-12 Years; Internal resistance 4,2 mOhm; Short cicuit current 3000A; Very lowgassing due to internal gas recombination (99% efficiency); Designed in accordance with IEC 60896-21/-22; Technical equal: 12SLA110L FIAMM | Pce | 32,00
9 | Valve Regulated Lead Acid BATTERY 12V - 150Ah | 12V, 150AH; Valve regulated lead acid compliance with IEC 60896 part 22 or BS 6290 part 4; Free maintenance, Electrolyte fully absorbed in glass mat "AGM" separator with extremely high micro porosity; Flame retardant plastics compliance with ABS IEC 707 or UL 94; Dimension L (483) x W (170) x H(240); Terminal: M8; Design life: 10-12 Years; Internal resistance lower than 4.5 mOhm; Designed in accordance with IEC 60896-21/-22 Technical equal : Fiamm 12SP150/ Vision 6FM150MV-X or Equal | Pce | 24,00
10 | Valve Regulated Lead Acid battery 400Ah; 2V c/w bolts and connectors | Valve Regulated Lead Acid battery (AGM) technology 2V; 400Ah c/w bolts and connectors; Dimension 250 x 220 x 226; Terminal: M8; Design life: 10-12 Years; Internal resistance 0.26 mOhm; Designed in accordance with IEC 60896-21/-22; Technical equal: 2SLA405 FIAMM | Set | 36,00
11 | DC UPS 220VAC/110VDC, 25A | DC UPS System With Diode Dropper And Battery: 1.Voltage Input 220VAC; +/- 10%; 1 phase; 2. Frequency: 50Hz; 3. Voltage Output: 110VDC; +/- 10%; 4. Current Output: 25A; C/w 01 MCCB input; 01 MCCB battery 32A; 03 MCCB output ( see drawing attactment); IP: 31; cable entry: top Entry; Measurement: Input/output ammeter and voltmeter; 5. Monitoring and protection: AC main; DC under/over voltage; Battery overcurrent; Dc earth fault; cooling fan failure; battery charger failure; Mode of control: floating; recharging; initial charge; Diode dropper; 6. Battery type: valve regulated lead acid; life time: 12 years; Min 180Ah; c.w battery rack. See more detail in Technical requirement. | Set | 1,00
12 | Battery charger, Input 240Vac, Output 24Vdc/ 50A | Battery charger for Solar Turbine 24 VDC 1. Voltage Input: 208-240VAC; 1 phase; 2. Frequency: 50/60Hz; 3. Voltage Output: 24VDC Nominal (27.1 VDC float) regulation: +/- 0.5% from no load to full load with +/-10% AC line variation; 4. Output current: 50A; c/w 01 CB input; 01 CB battery; 04 MCCB output (see drawing attactment); IP: 31; Cable entry: Bottom Entry; Measurement: DC voltmeter & ammeter 2%; 5. Monitoring and protection: AC input circuit breaker (2 pole); DC output circuit breaker (2 pole); Automatic current limiting; Slow start circuitry; AC and DC surge protection; Float/high-rate switch for manual control; 6. Part number: 65105-01 (american battery charging) or 190102-48272 (Solar Turbine) 7. Reference Model: CBC4-24-50/65158-01 or equivalant. | Set | 3,00
NOTE:
1 | Chất lượng hàng hóa: Hàng hóa mới 100%, chưa qua sử dụng, sản xuất không trước năm 2025.
2 | Thời gian và địa điểm giao hàng: Hàng hóa được giao không quá 02 lần và giao tại kho của LD Việt- Nga Vietsovpetro, số 67 đường 30/4, phường Rạch Rừa, TP Hồ Chí Minh.
3 | Bảo hành:
4 | Đóng gói hàng hóa:
5 | Yêu cầu về chứng chỉ:
+ Chứng chỉ xuất xứ (CO) được cấp bởi cơ quan có thẩm quyền của nước sản xuất hoặc nước xuất khẩu: Đối với hàng nhập khẩu trực tiếp: Bản gốc đối với hàng nhập khẩu trực tiếp. Đối với hàng không nhập trực tiếp: Bản sao có xác nhận của nhà nhập khẩu hoặc bản copy công chứng.
+ Chứng chỉ chất lượng (CQ) được cấp bởi nhà sản xuất: Đối với hàng nhập khẩu trực tiếp:Bản gốc giấy hoặc bản điện tử có thể truy xuất được. Đối với hàng không nhập trực tiếp: Bản sao công chứng/có xác nhận của nhà nhập khẩu hoặc bản điện tử có thể truy xuất được.
+ Biên bản kiểm tra chạy thử tại nhà sản xuất (FAT, SAT) đối với các mục 11, 12: bản gốc.
+ Chứng nhận phù hợp do tổ chức chứng nhận được công nhận cấp (như VR, ABS, BV, DNVGL, Lloyd) đối với các mục 11, 12: bản gốc.
+ Giấy chứng nhận bảo hành của nhà cung cấp: Bản gốc, đối với tất cả các mục hàng hóa.
PV&N TECH